## Question 4
Question 4 – amended February 1, 2021 Provide an Excel table of all distribution circuits existing in 2020 (as rows) that includes the following information in separate columns. Items (b) through (k) are features of the circuit. Items (l) through (bg) pertain to work performed for each circuit.
Mapped to Fire Safety Circuit Matrix List | Circuit Name | Circuit ID Number | Total Circuit Miles | Circuit Miles in non-High Fire Threat District (HFTD) Areas | Circuit Miles in HFTD Tier 2 | Circuit Miles in HFTD Tier 3 | Circuit Voltage (kV) | Wildfire Risk Level | Circuit SAIDI for 2020 | Circuit SAIFI for 2020 | Circuit MAIFI for 2020 | Miles of Enhanced Vegetation Management (EVM) Work in Non-High-Fire Threat District (HFTD) Areas in 2020 | Miles of EVM Work in HFTD Tier 2 in 2020 | Miles of EVM Work in HFTD Tier 3 in 2020 | Miles of Routine Vegetation Management Work in Non-High-Fire Threat District (HFTD) Areas in 2020 | Miles of Routine Vegetation Management work in HFTD Tier 2 in 2020 | Miles of Routine Vegetation Management work in HFTD Tier 3 in 2020 | Miles of Covered Conductor Installed in Non-HFTD in 2018 | Miles of Covered Conductor Installed in Non-HFTD in 2019 | Miles of Covered Conductor Installed in Non-HFTD in 2020 | Miles of Covered Conductor Installed in HFTD Tier 2 in 2018 | Miles of Covered Conductor Installed in HFTD Tier 2 in 2019 | Miles of Covered Conductor Installed in HFTD Tier 2 in 2020 | Miles of Covered Conductor Installed in HFTD Tier 3 in 2018 | Miles of Covered Conductor Installed in HFTD Tier 3 in 2019 | Miles of Covered Conductor Installed in HFTD Tier 3 in 2020 | Number of Poles Replaced in Non-HFTD in 2018 | Number of Poles Replaced in Non-HFTD in 2019 | Number of Poles Replaced in Non-HFTD in 2020 | Number of Poles Replaced HFTD Tier 2 in 2018 | Number of Poles Replaced HFTD Tier 2 in 2019 | Number of Poles Replaced HFTD Tier 2 in 2020 | Number of Poles Replaced HFTD Tier 3 in 2018 | Number of Poles Replaced HFTD Tier 3 in 2019 | Number of Poles Replaced HFTD Tier 3 in 2020 | Miles of Underground Conductor Installation in Non-HFTD in 2018 | Miles of Underground Conductor Installation in Non-HFTD in 2019 | Miles of Underground Conductor Installation in Non-HFTD in 2020 | Miles of Underground Conductor Installation in HFTD Tier 2 in 2018 | Miles of Underground Conductor Installation in HFTD Tier 2 in 2019 | Miles of Underground Conductor Installation in HFTD Tier 2 in 2020 | Miles of Underground Conductor Installation in HFTD Tier 3 in 2018 | Miles of Underground Conductor Installation in HFTD Tier 3 in 2019 | Miles of Underground Conductor Installation in HFTD Tier 3 in 2020 | Miles of LiDAR Inspection in Non-HFTD in 2020 | Miles of LiDAR Inspection in HFTD Tier 2 in 2020 | Miles of LiDAR Inspection in HFTD Tier 3 in 2020 | Number of Detailed Overhead Inspections in Non-HFTD in 2020 | Number of Detailed Overhead Inspections HFTD Tier 2 in 2020 | Number of Detailed Overhead Inspections HFTD Tier 3 in 2020 | Number of Sectionalization Devices Installed in Non-HFTD in 2018 | Number of Sectionalization Devices Installed in Non-HFTD in 2019 | Number of Sectionalization Devices Installed in Non-HFTD in 2020 | Number of Sectionalization Devices Installed HFTD Tier 2 in 2018 | Number of Sectionalization Devices Installed HFTD Tier 2 in 2019 | Number of Sectionalization Devices Installed HFTD Tier 2 in 2020 | Number of Sectionalization Devices Installed HFTD Tier 3 in 2018 | Number of Sectionalization Devices Installed HFTD Tier 3 in 2019 | Number of Sectionalization Devices Installed HFTD Tier 3 in 2020
Baldwin | BaldwinBreaker | NA | 9.44 | NA | 9.44 | 0 | 34.5 | 9062.28 | 856.272 | 9.1988 | 0 | NA | 3.129 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | NA | NA | NA | 0 | 1 | 9 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 9.44 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Boulder | BoulderBreaker | NA | 19.48 | NA | 19.48 | 0 | 4.16 | 9808.64 | 500.8514 | 4.869 | 0 | NA | 7.072 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 82 | 187 | 11 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 19.48 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Castle Glen (Division) | CastleGlen(Division)Breaker | NA | 10.61 | NA | 10.61 | 0 | 4.16 | 2685.52 | 3.0976 | 0.054714 | 0 | NA | 2.4255 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | NA | NA | NA | 2 | 8 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 10.61 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Clubview | ClubviewBreaker | NA | 10.45 | NA | 10.45 | 0 | 4.16 | 5058.14 | 168.8834 | 2.6714 | 0 | NA | 2.545 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 7 | 0 | 16 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 10.45 | NA | NA | 10.45 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Country Club | CountryClubBreaker | NA | 4.12 | NA | 4.12 | 0 | 4.16 | 1276.64 | 88.8843 | 2.2314 | 0 | NA | 0.159 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 1 | 4 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 4.12 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Eagle | EagleBreaker | NA | 8.91 | NA | 8.91 | 0 | 4.16 | 2840.24 | 0.50469 | 0.008342 | 0 | NA | 0.369 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 1 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 8.91 | NA | NA | 8.91 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Erwin Lake | ErwinLakeBreaker | NA | 29.24 | NA | 29.24 | 0 | 4.16 | 10899.34 | 4.5472 | 0.024872 | 0 | NA | 1.0915 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 10 | 125 | 192 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 29.24 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Fox Farm | FoxFarmBreaker | NA | 0.84 | NA | 0.84 | 0 | 4.16 | 0 | 0 | 0 | 0 | NA | 0 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 0.84 | NA | NA | 0.84 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Garstin | GarstinBreaker | NA | 8.91 | NA | 8.91 | 0 | 4.16 | 2179.32 | 0 | 0 | 0 | NA | 4.137 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0.82 | 0 | 0 | 0 | NA | NA | NA | 16 | 0 | 8 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 8.91 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Georgia | GeorgiaBreaker | NA | 9.86 | NA | 9.86 | 0 | 4.16 | 2460.68 | 32.3812 | 0.99218 | 0 | NA | 0.2955 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 9.86 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Geronimo (Bear Mtn.) | Geronimo(BearMountain)Breaker | NA | 0.03 | NA | 0.03 | 0 | 4.16 | 0 | 0 | 0 | 0 | NA | 0 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 0.03 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Goldmine | GoldmineBreaker | NA | 18.46 | NA | 18.46 | 0 | 4.16 | 7001.6 | 633.6547 | 4.0827 | 0 | NA | 9.24 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 18.46 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Harnish (Village) | Harnish(Village)Breaker | NA | 2.55 | NA | 2.55 | 0 | 4.16 | 767.52 | 262.7638 | 2.3976 | 0 | NA | 0.938 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 1 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 2.55 | NA | NA | 2.55 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Holcomb (Bear City) | Holcomb(BearCity)Breaker | NA | 14.1 | NA | 14.1 | 0 | 4.16 | 5954.75 | 0 | 0 | 0 | NA | 12.5875 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 14.1 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Interlaken | InterlackenBreaker | NA | 10 | NA | 10 | 0 | 4.16 | 2578.6 | 1.1205 | 0.019318 | 0 | NA | 0.9675 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 10 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Lagonita | LagonitaBreaker | NA | 8.89 | NA | 8.89 | 0 | 4.16 | 4127.58 | 338.5204 | 3.3645 | 0 | NA | 4.476 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 8.89 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Lift (Summit TOU) | ROOT | NA | 0.1 | NA | 0.1 | 0 | 4.16 | 32.8 | 0 | 0 | 0 | NA | 0 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 0.1 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
North Shore (Fawnskin) | NorthShore(Fawnskin)Breaker | NA | 23.92 | NA | 23.92 | 0 | 4.16 | 9307.34 | 0 | 0 | 0 | NA | 12.664 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 2 | 9 | 1 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 23.92 | NA | NA | 23.92 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Paradise | ParadiseBreaker | NA | 11.85 | NA | 11.85 | 0 | 4.16 | 4003.8 | 199.1937 | 1.0657 | 0 | NA | 5.91 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 6 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 11.85 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Pioneer (Palomino) | Pioneer(Palomino)Breaker | NA | 19.34 | NA | 19.34 | 0 | 4.16 | 4831.92 | 68.7773 | 0.64169 | 0 | NA | 0.8195 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 41 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 19.34 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Pump House (Lake) | PumpHouse(Lake)Breaker | NA | 0.66 | NA | 0.66 | 0 | 4.16 | 229.92 | 133.149 | 0.86592 | 0 | NA | 0.032 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 0.66 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Radford | RadfordBreaker | NA | 2.84 | NA | NA | 2.84 | 34.5 | 30732.36 | 0 | 0 | 0 | NA | NA | 0.141 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | 2.84 | NA | NA | 0 | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Shay | ShayBreaker(SCE Feed) | NA | 17.56 | NA | 17.56 | 0 | 34.5 | 13455.8 | 458.7937 | 6.6253 | 0 | NA | 2.5755 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0.5 | 3.32 | 0 | 0 | 0 | NA | NA | NA | 24 | 1 | 65 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 17.56 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Skyline (Summit Res) | SummitBreaker | NA | 0 | NA | 0 | 0 | 4.16 | 0 | 0 | 0 | 0 | NA | 0 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 0 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Sunrise (Maple) | Sunrise(Maple)Breaker | NA | 11.65 | NA | 11.65 | 0 | 4.16 | 4139.17 | 0.47477 | 0.0086321 | 0 | NA | 7.79 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 2 | 3 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 11.65 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Sunset | SunsetBreaker | NA | 11.17 | NA | 11.17 | 0 | 4.16 | 4721.41 | 0 | 0 | 0 | NA | 10.67 | NA | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA | NA | NA | 4 | 2 | 0 | NA | NA | NA | NA | NA | NA | 0 | 0 | 0 | NA | NA | NA | NA | 11.17 | NA | NA | 0 | NA | NA | NA | NA | 0 | 0 | 0 | 0 | 0 | 0
Based on GO 165 Detailed Inspection standards

## Q4. Supplemental - FSC Matrix
Circuit Information
A-D Columns added for this data request (i.e., not included in the Fire Safety Circuit Matrix calculations) |  |  |  | Algorithm Input = AI |  |  |  |  | AI | AI | AI | AI |  | AI |  |  |  | AI |  |  | AI | AI | AI | AI | AI
Tier 3 Total OH & UG | Tier 2 Total OH & UG | Total OH | Total OH & UG | Circuit | Substation | Wildfire Risk Group1 | Overall Risk Weighting | Risk Ranking | Voltage (kV) | High Fire Threat District Tier | Vegetation Density | Wind Intensity | # of Customers | # of Wood Poles | # of Fire Resistant Composite Poles | # of LWS Poles | # of Ductile Iron Poles | Bare Wire OH Circuit Miles | Covered Conductor OH Circuit Miles | UG Circuit Miles | # of Tree Attachments | # of Expulsion Fuses | # of Level 1 Deficiencies to be Corrected | # of Level 2 Deficiencies to be Corrected | Top Ten Worst Performing Circuit (1=Worst NR=Not Ranked)
NA | 9.44 | 8.94 | 9.44 | Baldwin | SCE Feed | 9062.28 | 0.065595 | 6 | 34.5 | 2 | High | High | 11305 | 256 | 0 | 0 | 0 | 8.61 | 0.33 | 0.5 | 0 | 0 | 0 | 0 | 2
NA | 19.48 | 17.68 | 19.48 | Boulder | Village | 9808.64 | 0.070997 | 4 | 4.16 | 2 | High | High | 2046 | 1007 | 0 | 0 | 0 | 17.68 | 0 | 1.8 | 86 | 30 | 0 | 0 | 5
NA | 10.61 | 6.93 | 10.61 | Castle Glen (Division) | Division | 2685.52 | 0.019438 | 16 | 4.16 | 2 | Mediun | Mediun | 1188 | 343 | 9 | 0 | 0 | 6.74 | 0.19 | 3.68 | 45 | 80 | 0 | 0 | NR
NA | 10.45 | 10.18 | 10.45 | Clubview | Moonridge | 5058.14 | 0.036612 | 9 | 4.16 | 2 | High | Mediun | 1984 | 508 | 0 | 0 | 0 | 10.18 | 0 | 0.27 | 88 | 0 | 0 | 2 | 9
NA | 4.12 | 3.18 | 4.12 | Country Club | Division | 1276.64 | 0.0092406 | 20 | 4.16 | 2 | Mediun | Mediun | 605 | 180 | 0 | 0 | 0 | 3.18 | 0 | 0.94 | 10 | 15 | 0 | 0 | 10
NA | 8.91 | 7.38 | 8.91 | Eagle | Pineknot | 2840.24 | 0.020558 | 15 | 4.16 | 2 | Mediun | Mediun | 959 | 323 | 0 | 0 | 0 | 7.38 | 0 | 1.53 | 16 | 104 | 0 | 0 | NR
NA | 29.24 | 21.83 | 29.24 | Erwin Lake | Maltby | 10899.34 | 0.078892 | 3 | 4.16 | 2 | High | High | 2533 | 1058 | 0 | 0 | 0 | 21.83 | 0 | 7.41 | 7 | 0 | 0 | 0 | NR
NA | 0.84 | 0 | 0.84 | Fox Farm | Meadow | 0 | 0 | 24 | 4.16 | 2 | Low | Mediun | 35 | 4 | 0 | 0 | 0 | 0 | 0 | 0.84 | 0 | 0 | 0 | 0 | NR
NA | 8.91 | 5.91 | 8.91 | Garstin | Meadow | 2179.32 | 0.015774 | 19 | 4.16 | 2 | Mediun | Mediun | 1055 | 277 | 0 | 0 | 0 | 5.09 | 0.82 | 3 | 15 | 124 | 0 | 1 | NR
NA | 9.86 | 5.91 | 9.86 | Georgia | Pineknot | 2460.68 | 0.017811 | 18 | 4.16 | 2 | Mediun | Mediun | 1023 | 348 | 0 | 0 | 0 | 5.91 | 0 | 3.95 | 63 | 76 | 0 | 0 | NR
NA | 0.03 | 0 | 0.03 | Geronimo (Bear Mtn.) | Bear Mtn. | 0 | 0 | 24 | 4.16 | 2 | Low | Mediun | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | NR
NA | 18.46 | 13.2 | 18.46 | Goldmine | Moonridge | 7001.6 | 0.050679 | 7 | 4.16 | 2 | High | Mediun | 1698 | 567 | 0 | 0 | 0 | 13.2 | 0 | 5.26 | 76 | 7 | 0 | 1 | 1
NA | 2.55 | 1.34 | 2.55 | Harnish (Village) | Village | 767.52 | 0.0055555 | 21 | 4.16 | 2 | Low | Mediun | 254 | 83 | 0 | 0 | 0 | 1.34 | 0 | 1.21 | 13 | 38 | 0 | 2 | NR
NA | 14.1 | 13.25 | 14.1 | Holcomb (Bear City) | Bear City | 5954.75 | 0.043102 | 8 | 4.16 | 2 | High | Mediun | 1587 | 615 | 0 | 0 | 0 | 13.25 | 0 | 0.85 | 33 | 109 | 0 | 0 | NR
NA | 10 | 6.45 | 10 | Interlaken | Meadow | 2578.6 | 0.018664 | 17 | 4.16 | 2 | Mediun | Mediun | 880 | 280 | 0 | 0 | 0 | 6.45 | 0 | 3.55 | 27 | 113 | 0 | 0 | NR
NA | 8.89 | 7.46 | 8.89 | Lagonita | Village | 4127.58 | 0.029876 | 13 | 4.16 | 2 | Mediun | High | 1103 | 453 | 0 | 0 | 0 | 7.46 | 0 | 1.43 | 60 | 116 | 0 | 1 | 7
NA | 0.1 | 0.1 | 0.1 | Lift (Summit TOU) | Summit | 32.8 | 0.00023741 | 23 | 4.16 | 2 | Low | Mediun | 1 | 1 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | NR
NA | 23.92 | 15.83 | 23.92 | North Shore (Fawnskin) | Fawnskin | 9307.34 | 0.067369 | 5 | 4.16 | 2 | High | High | 1523 | 923 | 0 | 0 | 0 | 15.83 | 0 | 8.09 | 56 | 0 | 0 | 7 | 6
NA | 11.85 | 9.85 | 11.85 | Paradise | Maltby | 4003.8 | 0.02898 | 14 | 4.16 | 2 | Mediun | Mediun | 1895 | 549 | 0 | 0 | 0 | 9.85 | 0 | 2 | 69 | 0 | 0 | 0 | 8
NA | 19.34 | 16.39 | 19.34 | Pioneer (Palomino) | Palomino | 4831.92 | 0.034975 | 10 | 4.16 | 2 | Low | Mediun | 537 | 602 | 0 | 0 | 0 | 13.89 | 2.5 | 2.95 | 0 | 38 | 0 | 2 | NR
NA | 0.66 | 0.64 | 0.66 | Pump House (Lake) | Lake | 229.92 | 0.0016642 | 22 | 4.16 | 2 | Low | Mediun | 4 | 22 | 0 | 0 | 0 | 0.64 | 0 | 0.02 | 0 | 10 | 0 | 0 | NR
2.84 | NA | 2.82 | 2.84 | Radford | SCE Feed | 30732.36 | 0.22245 | 1 | 34.5 | 3 | High | High | 3403 | 89 | 0 | 0 | 0 | 2.82 | 0 | 0.02 | 0 | 0 | 0 | 0 | NR
NA | 17.56 | 17.17 | 17.56 | Shay | SCE Feed | 13455.8 | 0.097396 | 2 | 34.5 | 2 | High | High | 9627 | 610 | 0 | 0 | 0 | 13.35 | 3.82 | 0.39 | 0 | 0 | 0 | 0 | 3
NA | 0 | 0 | 0 | Skyline (Summit Res) | Summit | 0 | 0 | 24 | 4.16 | 2 | Low | Mediun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NR
NA | 11.65 | 7.79 | 11.65 | Sunrise (Maple) | Maple | 4139.17 | 0.02996 | 12 | 4.16 | 2 | High | Mediun | 1506 | 348 | 0 | 0 | 0 | 7.79 | 0 | 3.86 | 36 | 0 | 0 | 0 | 4
NA | 11.17 | 10.67 | 11.17 | Sunset | Maple | 4721.41 | 0.034175 | 11 | 4.16 | 2 | High | Mediun | 1918 | 505 | 0 | 0 | 0 | 10.67 | 0 | 0.5 | 52 | 0 | 0 | 0 | NR
[6 empty] | 138155.37 | 1 | [6 empty] | 9951 | 9 | 0 | 0 | 203.24 | 7.66 | 54.08 | 752 | 860 | 0 | 16
Wildfire Risk Groups
High
Moderate
Low
[18 empty] | Bare Wire OH | Covered Conductor OH | UG | Total
[18 empty] | Circuit Miles | Circuit Miles | Circuit Miles | Circuit Miles
[17 empty] | 34 kV | 33.03 | 0.52 | 5.98 | 39.53
[17 empty] | 4 kV | 170.21 | 7.14 | 48.1 | 225.45
[17 empty] | Total | 203.24 | 7.66 | 54.08 | 264.98
[18 empty] | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles | Percent of Total Circuit Miles
[17 empty] | 34 kV | 12.47% | 0.1962% | 2.257% | 14.92%
[17 empty] | 4 kV | 64.24% | 2.695% | 18.15% | 85.08%
[17 empty] | Total | 76.7% | 2.891% | 20.41% | 100%
[18 empty] | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles | Percent of Total 34 kv Circuit Miles
[17 empty] | 34 kV | 83.56% | 1.315% | 15.13%
[18 empty] | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles | Percent of Total 4 kv Circuit Miles
[17 empty] | 4 kV | 75.5% | 3.167% | 21.34%

## Question 6
Question 6 For each WMP initiative listed below, please state how the Wildfire Risk Levels provided in the Excel spreadsheet for Questions 4 and 5 influenced where you performed work in 2020 and how work was sequenced.
WMP Initiative | WRL Influence Response
EVM | BVES chooses its projects based upon those most likely to reduce ignition probability and wildfire consequences based upon the evaluation from its Fire Safety Circuit Matrix (See tab for Q4). The FSCM identified 11 high risk circuits, 8 moderate risk circuits and 7 low risk circuits. The number of high risk circuits is planned to be reduced to 5 over the next 3 years and 0 in the next 10 years. All of BVES's vegetation management work is enhance vegetation management (EVM) due to BVES's entire service area being in the HFTD Tier 2 and 3. BVES EVM program trims its circuits approxiamtely every 2 years. The trim amount (minimum 12 feet) is designed to keep vegeation out of BVES's clearance limits until the next time the trimmed circuit is visited. BVES also performs LiDAR surveys annually and two GO-165 gorund patrols. When the results of these inspections reveal vegetation clearance issues or potential clearance issues, BVES dispatches vegetation crews to remidiate the issues.
Covered Conductor Installation | The covered conductor has been installed first along those circuits identified as High Risk circuits by the FSCM (See tab for Q4). BVES has not replaced bare wire with covered wire in its HFTD Tier 3 because this work is pending US Forestry Service permit approval. Once the permit is approved, BVES will commence pole replacements in its HFTD Tier 3 area.
Pole Replacement | The pole replacement efforts have been focused along those circuits identified as High Risk circuits by the FSCM (See tab for Q4), especially those where covered conductor was added. The additional weight from the covered conductor frequently requires new poles. BVES has not replaced poles in its HFTD Tier 3 because this work is pending US Forestry Service permit approval. Once the permit is approved, BVES will commence pole replacements in its HFTD Tier 3 area.
Undergrounding | BVES has not sought to underground any circuits as an initiative under the WMP. Further, BVES is not currently planning to underground any overhead facilities.
Grid Sectionalization | BVES has had sectionalization devices in place to limit the scope of PSPS to only the "higher risk" areas within its service area. Note that BVES's service area is all in the HFTD Tier 2 and 3; therefore, BVES further designated certain areas as "higher risk". These "higher risk" areas already had sectionalization devices in place. To date, BVES has not had to enact a PSPS activation.
Detailed Inspections of Distribution Assets | BVES conducts detailed inspections of all its distribution facilities in accordance with GO-165. Detailed inspections are conducted on a 5 year basis with circuits staggered so that each year several circuits are inspected. Per GO-165, BVES also conducts an annual patrol of all of its circuits. Additionally, because the entire BVES service territory is Tier 2 or Tier 3 HFTD, BVES believes additional inspections, beyond GO 165 and 174 are important for all of its above ground distribution assets. This includes LiDAR, a second 3rd party ground patrol, and, beginning 2021, UAV fly-over inspections.
Detailed Inspections of Transmission Assets | N/A
Aerial Inspections of Distribution Assets | BVES will undertake aerial inspections beginning in 2021 using UAVs. BVES's system is 211 circuit miles all in the HFTD; therefore, BVES will inspect the entire system as this is most cost effective while mitigating wildfire risk.
Aerial Inspections of Transmission Assets | N/A
LiDAR Inspections of Distribution Assets | BVES conducts an annually LiDAR inspection of its distribution facilities annually using truck-mounted LiDAR. BVES's system is 211 circuit miles all in the HFTD; therefore, BVES will inspect the entire system as this is most cost effective while mitigating wildfire risk.
LiDAR Inspections of Transmission Assets | N/A

## Question 7
Question 7 For each WMP initiative listed below, please complete Table A below, showing how much of the work you completed in 2020 was performed on distribution circuit-segments in each risk quintile.
Quintile Explanation | Top quintile of riskiest circuit-segments, which account for the first 20 percent of cumulative wildfire risk | Second quintile of riskiest circuit-segments, which account for percentiles 21 to 40 of cumulative wildfire risk | Third quintile of riskiest circuit-segments, which account for percentiles 41 to 60 of cumulative wildfire risk | Fourth quintile of riskiest circuit-segments, which account for percentiles 61 to 80 of cumulative wildfire risk | Last quintile of riskiest circuit-segments, which account for percentiles 81 to 100 of cumulative wildfire risk
Quintile of circuit-segments, ranked by wildfire risk | 0-20 | 21-40 | 41-60 | 61-80 | 81-100 | Total
Initiative | [6 empty] | Quintile
EVM | 23.54 | 28.321 | 31.6405 | 5.59 | 0.97 | 90.0615 | 0-20 | 21-40 | 41-60 | 61-80 | 81-100
Covered Conductor Installation | 7.8 | 0 | 0 | 0 | 0 | 7.8 | Boulder | Baldwin | Castle Glen (Division) | Country Club | Fox Farm
Pole Replacement | 269 | 66 | 0 | 8 | 1 | 344 | Erwin Lake | Clubview | Eagle | Garstin | Harnish (Village)
Undergrounding | 0 | 0 | 0 | 0 | 0 | 0 | North Shore (Fawnskin) | Goldmine | Lagonita | Georgia | Lift (Summit TOU)
Grid Sectionalization | 0 | 0 | 0 | 0 | 0 | 0 | Radford | Holcomb (Bear City) | Paradise | Geronimo (Bear Mtn.) | Pump House (Lake)
Detailed Inspections of Distribution Assets | 23.92 | 10.45 | 8.91 | 0 | 3.39 | 46.67 | Shay | Pioneer (Palomino) | Sunrise (Maple) | Interlaken | Skyline (Summit Res)
Detailed Inspections of Transmission Assets | NA | NA | NA | NA | NA | NA |  |  | Sunset
Aerial Inspections of Distribution Assets | 93.04 | 71.79 | 63.08 | 32.92 | 4.15 | 264.98
Aerial Inspections of Transmission Assets | NA | NA | NA | NA | NA | NA
LiDAR Inspections of Distribution Assets | 93.04 | 71.79 | 63.08 | 32.92 | 4.15 | 264.98
LiDAR Inspections of Transmission Assets | NA | NA | NA | NA | NA | NA

## Question 13
Question 13 Provide an Excel table of all defects in the year 2020 found by the Wildfire Safety Division’s Compliance Branch (as rows) that includes the following information in separate columns.
Defects in 2020 found by the WSD Compliance Branch (Finding #) | Associated Circuit Name | Defect Type | Description of Defect | WMP Initiative Associated with Defect | Date that defect was identified | Date that Defect was Corrected | Priority Level of Corresponding Corrective Tag | Location of Defect (Lat/Long)
1 | Not Provided by WSD Compliance Branch as part of Inspection Report | General | I verified Big Bear Dam weather station was installed at this location. The fuse was replaced by ELF Expulsion Limiting Fuse. CTC 1210284p HFTD 2 |  | 2020-10-27 | N/A | N/A | (34.2422864,-116.9777148)
2 | Not Provided by WSD Compliance Branch as part of Inspection Report | General | Hazard pine tree cut because of overhand over primary conductors. Pole #14207BVp HFTD 2 |  | 2020-10-27 | 2020-11-16 | 2 | (34.2488752,-116.966872)
3 | Not Provided by WSD Compliance Branch as part of Inspection Report | General | Vegetation clearance of pine tree next to pole 31476 CIT Pole #31476 CIT HFTD 2 |  | 2020-10-27 | 2020-11-16 | 2 | (34.2672571,-116.9368127)
4 | Not Provided by WSD Compliance Branch as part of Inspection Report | General | Next to 5150BV |  | 2020-10-27 | 2020-11-16 | 3 | (34.2721483,-116.9324322)
5 | Not Provided by WSD Compliance Branch as part of Inspection Report | GO95 General Order 95 Defect Code 1109 | 1109.1 ground wire broken or uncovered I verified the weather station was installed at this location Fawnskin Weather Station BV11050 |  | 2020-10-27 | 2020-11-16 | 3 | (34.2618513,-116.9253189)